| Design Report — Counter-flow heat exchanger (ε-NTU) Thermodynamics · Heat transfer · ε-NTU & LMTD methods | Esteban López Industrial Eng. 2026 |
| --- | --- |

1.  Problem & specification

Cool a hot process-water stream using cooling water in a counter-flow heat exchanger. Determine the heat duty, outlet temperatures and effectiveness, validate the result with an independent method, and quantify how the required area grows for a colder outlet.

| 90 / 20 °C hot / cold inlet | 2.0 / 2.5 kg/s hot / cold flow | 1200 W/m²K U (overall) | 8 m² area |
| --- | --- | --- | --- |

2.  Method — ε-NTU and LMTD

Capacity rates: C = m·cp. With C_min = 8,410 W/K (hot) and Cr = C_min/C_max = 0.805, the number of transfer units is NTU = U·A / C_min = 1.14. For a counter-flow exchanger the effectiveness is:

ε = (1 − e^[−NTU(1−Cr)]) / (1 − Cr·e^[−NTU(1−Cr)])      Q = ε·C_min·(Th,in − Tc,in)

The result is cross-checked with the LMTD method, Q = U·A·LMTD, which must agree. Fluid properties (cp) are taken from CoolProp at each stream’s mean temperature.

3.  Results

The ε-NTU operating point on the design chart, and the temperature profile along the exchanger:

| Quantity | Value |
| --- | --- |
| Effectiveness ε | 56.1 % |
| Heat duty Q (ε-NTU) | 330.3 kW |
| Heat duty Q (LMTD check) | 330.3 kW |
| Hot outlet temperature | 50.7 °C |
| Cold outlet temperature | 51.6 °C |
| LMTD | 34.4 °C |

ε-NTU and LMTD agree to within 1 % — an independent check that the calculation is consistent.

4.  Design trade-off

Inverting the problem (required area for a target hot-outlet temperature) shows diminishing returns: because effectiveness flattens at high NTU, cooling the hot stream below ~50 °C costs disproportionately more area. The current 8 m² already sits on the knee of the ε-NTU curve; reaching a 45 °C outlet would need roughly double the area. Fouling lowers U over time and shifts the operating point left, eroding effectiveness.

5.  Conclusion — engineering decisions enabled

Size for a target duty — choose area/U without over-building.

Choose the configuration — counter-flow beats parallel-flow effectiveness for the same area.

Plan for fouling — quantify the U decline and set a cleaning interval.

Optimise total cost — next step: add pressure-drop and pumping power to the trade-off.

Methods: ε-NTU and LMTD. Fluid properties via CoolProp. Fully reproducible in the attached notebook.