| Technical Report — Steam power plant (Rankine cycle) Thermodynamics · Power cycles · CoolProp (IAPWS-IF97) | Esteban López Industrial Eng. 2026 |
| --- | --- |

1.  Problem & specification

Analyse a steam power plant operating on a Rankine cycle. Compute every thermodynamic state, the thermal efficiency (ideal and with realistic component losses), the back-work ratio and the turbine-exit steam quality, and optimise the design by sweeping boiler pressure, superheat temperature and condenser pressure.

| 8 MPa boiler pressure | 500 °C turbine inlet | 10 kPa condenser | 0.85 / 0.85 turbine / pump η |
| --- | --- | --- | --- |

2.  Method

The four states are: 1 = condenser exit (saturated liquid), 2 = pump exit, 3 = turbine inlet (superheated), 4 = turbine exit. Enthalpies and entropies come from CoolProp (IAPWS-IF97). Efficiency:

η_th = w_net / q_in = (w_turbine − w_pump) / (h3 − h2)

3.  Results

| Quantity | Value |
| --- | --- |
| Ideal thermal efficiency | 39.4 % |
| Real thermal efficiency | 33.4 % |
| Net work | 1069 kJ/kg |
| Turbine work | 1079 kJ/kg |
| Pump work | 9.5 kJ/kg |
| Heat input q_in | 3198 kJ/kg |
| Back-work ratio | 0.88 % |
| Turbine-exit quality | 0.89 |

The back-work ratio of 0.88 % shows the pump consumes almost no work — the defining advantage of a vapour power cycle over a gas-turbine cycle.

4.  Optimisation & the wetness limit

Efficiency rises with superheat temperature and with lower condenser pressure (and with boiler pressure):

However, raising boiler pressure and lowering condenser pressure both push the turbine exit wetter. Below ~88 % quality, droplets erode the last turbine stages — the physical reason real plants use reheat (and regeneration).

5.  Conclusion

Fix the operating point — set pressures and superheat for a target efficiency.

Respect the wetness limit — it caps how far pressure and vacuum can be pushed.

Justify reheat & regeneration — the next design steps follow from this trade-off.

Benchmark vs Brayton — the <1% back-work ratio explains steam-cycle dominance in base-load power.

Steam properties via CoolProp (IAPWS-IF97). Fully reproducible in the attached notebook.